### ITEM MO-109  AIRPORT PREFABRICATED HOUSING AND EQUIPMENT

DESCRIPTION

109-1.1  This item shall consist of placing a prefabricated housing on a concrete pad in accordance with these specifications and the design and dimensions shown on the plans.  This work shall also include the installation of conduits in the concrete pad, lighting of the housing, and the furnishing of all incidentals necessary to produce a completed unit.  Included under this item or as a separate item where an existing enclosure is to be utilized shall be the furnishing of all equipment, wiring, electrical buses, cable, conduit, potheads, and grounding systems.  This work shall also include the painting of equipment and conduit; the marking and labeling of equipment and the labeling or tagging of wires; the testing of the installation; and the furnishing of all incidentals necessary to place it in operating condition as a completed unit to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

109-2.1  GENERAL.

a.  Airport lighting equipment and materials covered by Federal Aviation Administration (FAA) specifications shall be certified and listed under Advisory Circular (AC) 150/5345-53 (current version), Airport Lighting Equipment Certification Program.

b.  All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

c.  Manufacturer's certifications shall not relieve the Contractor of the Contractor’s responsibility to provide materials in accordance with these specifications and acceptable to the Engineer.  Materials supplied and/or installed that do not materially comply with these specifications shall be removed, when directed by the Engineer and replaced with materials, which do comply with these specifications, at the sole cost of the Contractor.

d.  All materials and equipment used to construct this item shall be submitted to the Engineer for approval prior to ordering the equipment.  Submittals consisting of marked catalog sheets or shop drawings shall be provided.  Submittal data shall be presented in a clear, precise and thorough manner.  Original catalog sheets are preferred.  Photocopies are acceptable provided they are as good a quality as the original.  Clearly and boldly mark each copy to identify pertinent products or models applicable to this project.  Indicate all optional equipment and delete non-pertinent data.  Submittals for components of electrical equipment and systems shall identify the equipment for which they apply on each submittal sheet.  Markings shall be boldly and clearly made with arrows or circles (highlighting is not acceptable).  Contractor is solely responsible for delays in project accruing directly or indirectly from late submissions or resubmissions of submittals.

e.  The data submitted shall be sufficient, in the opinion of the Engineer, to determine compliance with the plans and specifications.  The Contractor's submittals (five (5) copies) shall be neatly bound in a properly sized 3-ring binder, tabbed by specification section.  The Engineer reserves the right to reject any and all equipment, materials or procedures, which, in the Engineer’s opinion, does not meet the system design and the standards and codes, specified herein.

f.  All equipment and materials furnished and installed under this section shall be guaranteed against defects in materials and workmanship for a period of at least twelve (12) months from final acceptance by the Owner.  The defective materials and/or equipment shall be repaired or replaced, at the Owner's discretion, with no additional cost to the Owner.

109-2.2  CONCRETE.  The concrete for the housing shall be proportioned, placed, and cured in accordance with Item MO-610 “Structural Portland Cement Concrete.”

109-2.3  REINFORCING STEEL.  Reinforcing steel bars shall be intermediate or structural grade deformed-type bars and shall meet the requirements of ASTM A 615.

109-2.4  RIGID STEEL CONDUIT.  Rigid steel conduit and fittings shall be in accordance with Underwriters Laboratories Standard 6 and 514.

109-2.5  LIGHTING.  Housing light fixtures shall be of a vaporproof type.

109-2.6  OUTLETS.  Convenience outlets shall be heavy-duty duplex units designed for industrial service.

109-2.7  SWITCHES.  Housing light switches shall be single-pole switches.

109-2.8  PAINT.

a.  Priming paint for ungalvanized metal surfaces shall be a high solids alkyd primer conforming to TT-P-664D.

b.  White paint for body and finish coats on metal and wood surfaces shall be ready-mixed paint conforming to the Master Painter’s Institute, Reference #9, Exterior Alkyd, Gloss, VOC Range E2.

c.  Priming paint for wood surfaces shall be mixed on the job by thinning the above specified white paint by adding 1/2 pint (0.06 liter) of raw linseed oil to each gallon (liter).

109-2.9  HIGH-VOLTAGE BUS.  High-voltage bus shall be standard weight 3/8-inch IPS copper tubing or it may be insulated copper cable of the size and voltage rating specified.

109-2.10  BUS CONNECTORS.  Connectors shall be similar to Burndy Type NT (or equivalent) for copper tubing.  Connectors for insulated bus cable shall be of the proper size and type for the service intended.

109-2.11  BUS SUPPORTS.  Bus supports shall be similar to Westinghouse No. 527892 (or equivalent), insulated for 7,500 volts, single clamp type for 2-bolt flat mounting.

109-2.12  GROUND BUS.  Ground bus shall be 1/8 - x ¾-inch minimum copper bus bar.

109-2.13  SQUARE DUCT.  Duct shall be square similar to that manufactured by the Square D Company (or equivalent), or the Trumbull Electric Manufacturing Company (or equivalent).  The entire front of the duct on each section shall consist of hinged or removable cover for ready access to the interior.  The cross section of the duct shall be not less than 4 x 4 inches except where otherwise shown in the plans.

109-2.14  GROUND CONNECTION AND GROUND ROD.  The Contractor shall furnish and install ground rods, grounding cable, and ground clamps for grounding as shown on the plans.  The ground rod shall be of the type specified in Item MO-108 “Underground Power Cable for Airports and shall be of the length and diameter specified on the plans.  The ground rod shall be driven into the ground adjacent to the concrete pad as shown on the plans so that the top is at least 6 inches below grade.  The grounding cable shall be firmly attached to the ground rod by exothermic welding per MO-108.  The resistance to ground shall not exceed 25 ohms.

109-2.15  POTHEADS.  Potheads shall be similar to G&W Type N, Shape C (or equivalent), unless otherwise specified.  Potheads shall be furnished with plain insulator bushings and conduit couplings.  Potheads shall have a rating not less than the circuit voltage.

109-2.16  PREFABRICATED HOUSING.  The prefabricated housing shall be a commercially available unit as shown on the plans.

109-2.17  FAA-APPROVED EQUIPMENT.  Certain items of airport lighting equipment installed in housings are covered by individual FAA equipment specifications.  The specifications are listed below:

AC 150/5345-3	Specification for L-821 Panels for Remote Control of Airport Lighting

AC 150/5345-5	Circuit Selector Switch

AC 150/5345-7	Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-10	Specification for Constant Current Regulators and Regulator Monitors

AC 150/5345-13	Specification for L-841 Auxiliary Relay Cabinet Assembly for Pilot Control of Airport Lighting Circuits.

AC 150/5345-49	Specification L-854 Radio Control Equipment

109-2.18  OTHER ELECTRICAL EQUIPMENT.  Constant-current regulators, distribution transformers, oil switches, cutouts, relays, terminal blocks, transfer relays, circuit breakers, and all other regularly used commercial items of electrical equipment not covered by FAA equipment specifications shall conform to the applicable rulings and standards of the Institute of Electrical and Electronic Engineers or the National Electrical Manufacturers Association.  When specified, test reports from a testing laboratory indicating that the equipment meets the specifications shall be supplied. In all cases, equipment shall be new and a first-grade product.  This equipment shall be supplied in the quantities required for the specific project and shall incorporate the electrical and mechanical characteristics specified in the proposal and plans.

109-2.19  WIRE.  Wire in conduit rated up to 5,000 volts shall conform to AC 150/5345-7, Specification for L-824 Underground Electrical Cables for Airport Lighting Circuits, for rubber insulated neoprene-covered wire, or Fed. Spec. J-C-30, Type RHW, for rubber insulated fibrous-covered wire.  For ratings up to 600 volts, thermoplastic wire conforming to Fed. Spec. J-C-30, Types TW, THW, and THWN, shall be used.  The wires shall be of the type, size, number of conductors, and voltage shown in the plans or in the proposal.

a.  Control Circuits.  Unless otherwise indicated on the plans, wire shall be not less than No. 12 AWG and shall be insulated for 600 volts.  If telephone control cable is specified, No. 19 AWG telephone cable conforming to ICEA S-85-625-1996 specifications shall be used.

b.  Power Circuits.

(1)  600 volts maximum-Wire shall be No. 6 AWG or larger and insulated for at least 600 volts.

(2)  3,000 volts maximum-Wire shall be No. 6 AWG or larger and insulated for at least 3,000 volts.

(3)  Over 3,000 volts-Wire shall be No. 6 AWG or larger and insulated for at least the circuit voltage.

109-2.20   CONSTANT CURRENT REGULATOR.    The constant current regulator shall be a Type L-828, ferroresonant design, conforming to the requirements of AC 150/5345-10.  The regulator shall be the size as shown on the plans and floor mounted.  Single phase, 6.6A maximum output current, 60 Hz, taps for 208, 220, and 240 volts shall be provided.  Brightness selection relays shall be interlocked to prevent simultaneous operation.  The output current shall be constant under all ambient temperatures.  Mounting bolts and pattern shall be in accordance with manufacturer’s recommendation.  Lightning protection shall be provided on the input and output of the regulator. A percent brightness control switch shall be prewired on the regulators as specified in Section 109-2.21 and 109-2.22.  The regulator shall have an integrated series plug cutout.  See the plans for details.

109-2.21  SWITCHES (Lighting Circuit).  A five-position switch selector switch with manual return, contact blocks and legend plate shall be provided for the percent brightness control switch.  The percent brightness control switch shall be prewired as part of the regulator assembly.  Legend plates shall be phenolic plastic with black fields and the following 1/8-inch high characters engraved in white:

##### Percent Brightness

##### Remote-Off-10-30-100

109-2.22  SWITCHES (P.A.P.I. Circuit).  A seven-position switch selector switch with manual return, contact blocks and legend plate shall be provided for the percent brightness control switch.  The percent brightness control switch shall be prewired as part of the regulator assembly.  Legend plates shall be phenolic plastic with black fields and the following 1/8-inch high characters engraved in white:

##### Percent Brightness

Remote-Off-1-2-3-4-5

CONSTRUCTION METHODS

109-3.1  GENERAL.  The Contractor shall place the prefabricated housing at the location indicated in the plans.  The housing shall be a prefabricated equipment enclosure supplied in the size specified. The concrete pad, installation methods, and equipment placement are shown in the plans.

The Contractor shall clear, grade, and seed the area around the housing for a minimum distance of 10 feet on all sides.  The slope shall be not less than ½-inch per foot away from the housing in all directions.

The housing shall provide adequate protection against weather elements, including rain, wind-driven dust, snow, ice and excessive heat.  The housing shall have sufficient filtered ventilation, to assure that the interior room temperatures and conditions do not exceed the recommended limits of the electrical equipment to be installed in the housing.  Contractor is responsible for contacting the manufacturer of the equipment to be installed to obtain environmental limitations of the equipment to be installed.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The prefabricated housing shall provide reasonable protection of the equipment that it is intended to house.  As most of the equipment located in the housing is likely housed in NEMA 1 enclosures, the housing itself shall be designed to provide sufficient protection against weather elements.

Assure that the housing that is to be supplied has sufficient environmental controls to provide adequate ventilation to maintain temperatures within operational requirements of equipment to be installed.  In addition, make sure that the housing has sufficient seals and/or filters on doors and other openings to assure that wind-driven dust does not affect operation of equipment.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

109-3.2  CONCRETE PAD.  The contractor shall construct the reinforced concrete pad in accordance with the details shown in the plans. Reinforcing steel shall be placed, as shown in the plans, and secured in position to prevent displacement during the concrete placement.

109-3.3  CONDUITS IN CONCRETE PAD.  Conduits shall be installed in the concrete pad in accordance with the details shown in the plans. All underground conduit shall be painted with a bituminous compound. Conduit shall be installed with a coupling or metal conduit adapter flush with the top of the floor. All incoming conduit shall be closed with a pipe plug to prevent the entrance of foreign material during construction. Space conduit entrances shall be left closed.

EQUIPMENT INSTALLATION IN PREFABRICATED HOUSING

109-4.1 GENERAL.  The Contractor shall furnish, install, and connect all equipment, equipment accessories, conduit, cables, wires, buses, grounds, and support necessary to insure a complete and operable electrical distribution center for the airport lighting system as specified herein and shown in the plans.  When specified, an emergency power supply and transfer switch shall be provided and installed.

The equipment installation and mounting shall comply with the requirements of the National Electrical Code and local code agency having jurisdiction.

109-4.2  POWER SUPPLY EQUIPMENT.  Transformers, regulators, booster transformers, and other power supply equipment items shall be furnished and installed at the location shown in the plans or as directed by the Engineer.  The power supply equipment shall be set on steel  “H” sections,  “I” beams, channels, or concrete blocks to provide a minimum space of 1-½ inches between the equipment and the floor. The equipment shall be placed so as not to obstruct the oil-sampling plugs of the oil-filled units; and name-plates shall, so far as possible, not be obscured.

If specified in the plans and specifications, equipment for an alternate power source or an emergency power generator shall be furnished and installed.  The alternate power supply installation shall include all equipment, accessories, an automatic changeover switch, and all necessary wiring and connections.  The emergency power generator set shall be the size and type specified.

109-4.3  SWITCHGEAR AND PANELS.  Oil switches, fused cutouts, relays, transfer switches, panels, panel boards, and other similar items shall be furnished and installed at the location shown in the plans or as directed by the Engineer.  Items shall be attached to the wall with stainless steel or cadium-plated hardware.

109-4.4  DUCT AND CONDUIT.  The Contractor shall furnish and install square-type exposed metallic ducts with hinged covers for the control circuits in the housing.  These shall be mounted along the walls behind all floor-mounted equipment and immediately below all wall-mounted equipment.  The hinged covers shall be placed to open from the front side with the hinges at the front bottom.

Wall brackets for square ducts shall be installed at all joints 2 feet or more apart with intermediate brackets as specified.  Conduit shall be used between square ducts and equipment or between different items of equipment when the equipment is designed for conduit connection.  When the equipment is not designed for conduit connection, conductors shall enter the square-type control duct through insulating bushings in the duct or on the conduit risers.

109-4.5  CABLE ENTRANCE AND HIGH-VOLTAGE BUS SYSTEM.  Incoming underground cable from field circuits and supply circuits will be installed outside the walls of the housing as a separate item under Item MO-108 “Underground Power Cable for Airports.”  The Contractor installing the equipment shall bring the cables from the trench or duct through the entrance conduits into the housing and make the necessary electrical connections.  For the incoming and outgoing high voltage load circuits, the Contractor shall furnish and install rigid metallic vi conduit risers, surmounted by potheads, from floor level to the level as shown in the plans.

The incoming high-voltage power supply service to the housing shall enter below the floor of the housing and shall rise from the floor level in a rigid metallic conduit riser, surmounted by a pothead, as described above.  Using insulated high-voltage cable, the incoming power service shall be connected from the pothead to the oil-fused cutouts or to the specified disconnecting switch or equipment.  From the oil-fused cutouts or disconnecting device, the insulated service conductors shall be connected to the overhead voltage bus system of the housing.  The high-voltage bus system shall utilize the materials specified and shall be mounted and installed in accordance with the requirements of the National Electrical Code or the local code agency having jurisdiction.

109-4.6  WIRING AND CONNECTIONS.  The Contractor shall make all necessary electrical connections in the housing in accordance with the wiring diagrams furnished and as directed by the Engineer.  In wiring to the terminal blocks, the Contractor shall leave sufficient extra length on each control lead to make future changes in connections at the terminal block.  This shall be accomplished by running each control lead the longest way around the box to the proper terminal.  Leads shall be neatly laced in place.

109-4.7  MARKING AND LABELING.  All equipment, control wires, terminal blocks, etc., shall be tagged, marked, or labeled as specified below:

a.  Wire Identification.  The Contractor shall furnish and install self-sticking wire labels or identifying tags on all control wires at the point where they connect to the control equipment or to the terminal blocks.  Wire labels, if used, shall be of the self-sticking preprinted type and of the manufacturer's recommended size for the wire involved.  Identification -markings designated in the plans shall be followed.  Tags, if used, shall be of fiber not less than ¾-inch in diameter and not less than 1/32-inch thick.  Identification markings designated in the plans shall be stamped on tags by means of smalltool dies.  Each tag shall be securely tied to the proper wire by a nonmetallic cord.

b.  Labels.  The Contractor shall stencil identifying labels on the cases of regulators, breakers, and distribution and control relay cases with white oil paint as designated by the Engineer.  The letters and numerals shall be not less than 1 inch in height and shall be of proportionate width.  The Contractor shall also mark the correct circuit designations in accordance with the wiring diagram on the terminal marking strips, which are a part of each terminal block.

109-4.8  TESTING.  The installation shall be tested in operation as a completed unit prior to acceptance in accordance with 108-3.8 in Item MO-108 “Underground Power Cable for Airports.”. The contractor shall furnish the testing equipment. Tests shall be conducted in the presence of the engineer and shall be to his/her satisfaction.

METHOD OF MEASUREMENT

109-5.1  The quantity to be paid for under this item shall consist of the prefabricated housing constructed in place and the equipment installed, connected, and accepted as a complete unit ready for operation.

BASIS OF PAYMENT

109-6.1  Payment will be made at the contract unit price for each completed and accepted job.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete the item.

Payment will be made under:

Item MO-109-6.1  Airport Prefabricated Housing and Equipment -- per Lump Sum

MATERIAL REQUIREMENTS

AC 150/5345-3	Specification for L-821 Panels for Remote Control of Airport Lighting

AC 150/5345-5	Circuit Selector Switch

AC 150/5345-7	Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-10	Specification for Constant Current Regulators and Regulator Monitors

AC 150/5345-13	Specification for L-841 Auxiliary Relay Cabinet Assembly for Pilot Control of Airport Lighting Circuits

AC 150/5345-49	Specification L-854 Radio Control Equipment

ANSI/ICEA S-85-625-1996	Aircore, Polyethylene Insulated, Copper Conductor, Telecommunications Cable

ASTM A 615	Specification for Deformed and Plain Billet Steel Bars for Concrete Reinforcement

FED SPEC J-C-30	Cable and Wire, Electrical (Power, Fixed Installation) (cancelled; replaced by AA-59544 Cable and Wire, Electrical (Power, Fixed Installation))

Underwriters Laboratories	Rigid Metal Conduit

Standard 6

Underwriters Laboratories	Fittings for Conduit and Outlet Boxes

Standard 514

Master Painter’s Institute

### REFERENCE DOCUMENTS

NFPA No. 70			National Electrical Code (NEC)