ITEM MO-110  AIRPORT UNDERGROUND ELECTRICAL DUCT BANKS AND CONDUITS

DESCRIPTION

110-1.1  This item shall consist of underground electrical conduits and duct banks (single or multiple conduits encased in concrete) installed in accordance with this specification at the locations and in accordance with the dimensions, designs, and details shown on the plans.  This item shall include furnishing and installing of all underground electrical duct banks and individual and multiple underground conduits.  It shall also include all turfing trenching, backfilling, removal, and restoration of any paved or turfed areas; concrete encasement, mandreling, pulling lines, duct markers, plugging of conduits, and the testing of the installation as a completed system ready for installation of cables in accordance with the plans and specifications.  This item shall also include furnishing and installing conduits and all incidentals for providing positive drainage of the system.  Verification of existing ducts is incidental to the pay items provided in this specification.

EQUIPMENT AND MATERIALS

110-2.1  GENERAL.

a.  All equipment and materials covered by referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when so requested by the Engineer.

b.  Manufacturer's certifications shall not relieve the Contractor of the Contractor’s responsibility to provide materials in accordance with these specifications and acceptable to the Engineer.  Materials supplied and/or installed that do not materially comply with these specifications shall be removed, when directed by the Engineer and replaced with materials, which do comply with these specifications, at the sole cost of the Contractor.

c.  All materials and equipment used to construct this item shall be submitted to the Engineer for approval prior to ordering the equipment.  Submittals consisting of marked catalog sheets or shop drawings shall be provided.  Submittal data shall be presented in a clear, precise and thorough manner.  Original catalog sheets are preferred.  Photocopies are acceptable provided they are as good a quality as the original.  Clearly and boldly mark each copy to identify pertinent products or models applicable to this project.  Indicate all optional equipment and delete non-pertinent data.  Submittals for components of electrical equipment and systems shall identify the equipment for which they apply on each submittal sheet.  Markings shall be boldly and clearly made with arrows or circles (highlighting is not acceptable).  Contractor is solely responsible for delays in project accruing directly or indirectly from late submissions or resubmissions of submittals.

d.  The data submitted shall be sufficient, in the opinion of the Engineer, to determine compliance with the plans and specifications.  The Contractor's submittals (five (5) copies) shall be neatly bound in a properly sized 3-ring binder, tabbed by specification section.  The Engineer reserves the right to reject any and all equipment, materials or procedures, which, in the Engineer’s opinion, does not meet the system design and the standards and codes, specified herein.

e.  All equipment and materials furnished and installed under this section shall be guaranteed against defects in materials and workmanship for a period of at least twelve (12) months from final acceptance by the Owner.  The defective materials and/or equipment shall be repaired or replaced, at the Owner's discretion, with no additional cost to the Owner.

110-2.2  STEEL CONDUIT.  Rigid galvanized steel conduit and fittings shall be hot dipped galvanized inside and out and conform to the requirements of Underwriters Laboratories Standard 6, 514B, and 1242.

110-2.3 PLASTIC CONDUIT.  Plastic conduit and fittings-shall conform to the requirements of Fed. Spec. W--C-1094, Underwriters Laboratories Standards UL-651 and Article 347 of the current National Electrical Code shall be one of the following, as shown on the plans:

a. Type I–Schedule 40 PVC suitable for underground use either direct-buried or encased in concrete.

b. Type II–Schedule 40 PVC suitable for either above ground or underground use.

c. High Density Polyethylene pipe (HDPE) meeting requirements of ASTM D 2160 Schedule 40 if in earth, schedule 80 if under pavements.

*************************************************************************************

NOTE TO SPECIFIER: HDPE may be used under pavements when conduit placed with directional boring.

*************************************************************************************

The type of adhesive shall be as recommended by the conduit/fitting manufacturer.

110-2.4 SPLIT CONDUIT.  Split conduit shall be pre-manufactured for the intended purpose and shall be made of steel or plastic.

110-2.5 CONDUIT SPACERS.  Conduit spacers shall be prefabricated interlocking units manufactured for the intended purpose.  They shall be of double wall construction made of high grade, high density polyethylene complete with interlocking cap and base pads, They shall be designed to accept No. 4 reinforcing bars installed vertically.

110-2.6 CONCRETE.  The concrete for conduit shall be proportioned, placed, and cured in accordance with Item MO-610 “Structural Portland Cement Concrete.”  Where reinforced duct banks are specified, reinforcing steel shall conform to ASTM A 615 Grade 60.  Concrete and reinforcing steel are incidental to the respective pay item of which they are a component part.

110-2.7 FLOWABLE BACKFILL.  Flowable material used to back fill conduit and duct bank trenches shall conform to the requirements of Item P-153 "Controlled Low Strength Material".

110-2.8  DETECTABLE WARNING TAPE.  Red plastic, detectable, magnetic tape shall be polyethylene film with a metallized foil core 4-6 inches wide and imprinted with the words “Caution Buried Electric Line Below”.  Detectable tape is incidental to the respective bid item.

CONSTRUCTION METHODS

110-3.1  GENERAL.  The Contractor shall install underground duct banks and conduits at the approximate locations indicated on the plans.  The Engineer shall indicate specific locations as the work progresses, if required to differ from the plans.  Duct banks and conduits shall be of the size, material, and type indicated on the plans or specifications.  Where no size is indicated on the plans or in the specifications, conduits shall be not less than 2 inches inside diameter or comply with the National Electrical Code based on cable to be installed, whichever is larger.  All duct bank and conduit lines shall be laid so as to grade toward access points and duct or conduit ends for drainage.  Unless shown otherwise on the plans, grades shall be at least 3 inches per 100 feet.  On runs where it is not practicable to  maintain the grade all one way, the duct bank and conduit lines shall be graded from the center in both directions toward access points or conduit ends, with a drain into the storm drainage system.  Pockets or traps where moisture may accumulate shall be avoided.  No duct bank or underground conduit shall be less than 18 inches below finished grade.  Where under pavement, the top of the duct bank shall not be less than 18 inches below the subgrade.

The Contractor shall mandrel each individual conduit whether the conduit is direct-buried or part of a duct bank.  An iron-shod mandrel, not more than 1/4-inch smaller than the bore of the conduit shall be pulled or pushed through each conduit.  The mandrel shall have a leather or rubber gasket slightly larger than the conduit hole.

The Contractor shall swab out all conduits/ducts and clean base can, manhole, pull boxes, etc. interiors IMMEDIATELY prior to pulling cable.  Once cleaned and swabbed the base cans, manhole, pull boxes, etc. and all accessible points of entry to the duct/conduit system shall be kept closed except when installing cables.  Cleaning of ducts, base cans, manholes, etc. is incidental to the pay item of the item being cleaned.  All raceway systems left open, after initial cleaning, for any reason shall be recleaned at the Contractor’s expense.  All accessible points shall be kept closed when not installing cable.  The Contractor shall verify existing ducts proposed for use in this project as clear and open.  The Contractor shall notify the Engineer of any blockage in the existing ducts.

For pulling the permanent wiring, each individual conduit, whether the conduit is direct-buried or part of a duct bank, shall be provided with a 200 pound test polypropylene pull rope.  The ends shall be secured and sufficient length shall be left in access points to prevent it from slipping back into the conduit.  Where spare conduits are installed, as indicated on the plans, the open ends shall be plugged with removable tapered plugs, designed for this purpose.

All conduits shall be securely fastened in place during construction and shall be plugged to prevent contaminate from entering the conduits.  Any conduit section having a defective joint shall not be installed.  Ducts shall be supported and spaced apart using approved spacers at intervals not to exceed 5 feet.

Unless otherwise shown on the plans, concrete encased duct banks shall be utilized when crossing under pavements expected to carry aircraft loads.

Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored.

Trenches for conduits and duct banks may be excavated manually or with mechanical trenching equipment unless in pavement, in which case they shall be excavated with mechanical trenching equipment.  Walls of trenches shall be essentially vertical so that a minimum of shoulder surface is disturbed.  Blades of graders shall not be used to excavate the trench.

When rock is encountered, the rock shall be removed to a depth of at least 3 inches below the required conduit or duct bank depth and it shall be replaced with bedding material of earth or sand containing no mineral aggregate particles that would be retained on a 1/4-inch sieve.  Flowable backfill may alternatively be used The Contractor shall ascertain the type of soil or rock to be excavated before bidding.  All excavation shall be unclassified.  Unclassified excavation will consist of the excavation of all material of whatever character encountered in the work.

Underground electrical warning (caution) tape shall be installed in the trench above all underground duct banks and conduits in unpaved areas.  Contractor shall submit a sample of the proposed warning tape for approval by the Engineer.  If not shown on the plans, the warning tape shall be located six inches above the duct/conduit.

Joints in plastic conduit shall be prepared in accordance with the manufacturer's recommendations for the particular type of conduit.  Plastic conduit shall be prepared by application of a plastic cleaner and brushing a plastic solvent on the outside of the conduit ends and on the inside of the couplings.  The conduit fitting shall then be slipped together with a quick one-quarter turn twist to set the joint tightly.  Where more than one conduit is placed in a single trench, or in duct banks, joints in the conduit shall be staggered a minimum of 2 feet.

Changes in direction of runs exceeding 10 degrees, either vertical or horizontal, shall be accomplished using manufactured sweep bends.

Whether or not specifically indicated on the drawings, where the soil encountered at established duct bank grade is an unsuitable material, as determined by the Engineer, the unsuitable material shall be removed in accordance with Item MO-152 and replaced with suitable material.  Alternatively, additional duct bank supports that are adequate and stable shall be installed, as approved by the Engineer.

All excavation shall be unclassified and shall be considered incidental to the respective MO-110 pay item of which it is a component part.  Dewatering necessary for duct installation, erosion and turbidity control, in accordance with Federal, State, and Local requirements is incidental to its respective pay item as a part of Item MO-110.  The cost of all excavation regardless of type of material encountered, shall be included in the unit price bid for the MO-110 Item.

Unless otherwise specified, excavated materials that are deemed by the Engineer to be unsuitable for use in backfill or embankments shall be removed and disposed of off site.

Any excess excavation shall be filled with suitable material approved by the Engineer and compacted in accordance with item MO-152.

It is the Contractor's responsibility to locate existing utilities within the work area prior to excavation.  Where existing active cables) cross proposed installations, the Contractor shall insure that these cable(s) are adequately protected.  Where crossings are unavoidable, no splices will be allowed in the existing cables, except as specified on the plans.  Installation of new cable where such crossings must occur shall proceed as follows:

(1)	Existing cables shall be located manually.  Unearthed cables shall be inspected to assure absolutely no damage has occurred.

(2)	Trenching, etc., in cable areas shall then proceed with approval of the Engineer, with care taken to minimize possible damage or disruption of existing cable, including careful backfilling in area of cable.

In the event that any previously identified cable is damaged during the course of construction, the Contractor shall be responsible for the complete repair.

110-3.2  DUCT BANKS.  Unless otherwise shown in the plans, duct banks shall be installed so that the top of the concrete envelope is not less than 18 inches below the bottom of the base or stabilized base course layers where installed under runways, taxiways, aprons, or other paved areas, and not less than 18 inches below finished grade where installed in unpaved areas.

Unless otherwise shown on the plans, duct banks under paved areas shall extend at least 3 feet beyond the edges of the pavement or 3 feet beyond any underdrains that may be installed alongside the paved area.  Trenches for duct banks shall be opened the complete length before concrete is placed so that if any obstructions are encountered, proper provisions can be made to avoid them.  Unless otherwise shown on the plans, all duct banks shall be placed on a layer of concrete not less than 3 inches thick prior to its initial set.  Where two or more conduits in the duct bank are intended to carry conductors of equivalent voltage insulation rating, the Contractor shall space the conduits not less than 1-1/2 inches apart (measured from outside wall to outside wall).  Where two or more conduits in the duct bank are intended to carry conductors of differing voltage insulation rating, the Contractor shall space the conduits not less than 3 inches apart (measured from outside wall to outside wall).  All such multiple conduits shall be placed using conduit spacers applicable to the type of conduit.  As the conduit laying progresses, concrete shall be placed around and on top of the conduits not less than 3 inches thick unless otherwise shown on the plans.  End bells or couplings shall be installed flush with the concrete encasement at access points.

Conduits forming the duct bank shall be installed using conduit spacers.  No. 4 reinforcing bars shall be driven vertically into the soil a minimum of 6 inches to anchor the assembly into the earth prior to placing the concrete encasement.  For this purpose, the spacers shall be fastened down with locking collars attached to the vertical bars.  Spacers shall be installed at 5 -foot intervals. Spacers shall be in the proper sizes and configurations to fit the conduits.  Locking collars and spacers shall be submitted to the Engineer for review prior to use.

When specified, the Contractor shall reinforce the bottom side and top of encasements with steel reinforcing mesh or fabric or other approved metal reinforcement.  When directed, the Contractor shall supply additional supports where the ground is soft and boggy, where ducts cross under roadways, or where shown on the plans.  Under such conditions, the complete duct structure shall be supported on reinforced concrete footings, piers, or piles located at approximately 5 foot intervals.

All pavement surfaces that are to have ducts installed therein shall be neatly saw cut to form a vertical face.  All excavation shall be included in the contract with price for the duct.

Install a plastic, detectable, color as noted, 4-6 inch wide tape 8 inches minimum below grade above all underground conduit or duct lines not installed under pavement.

When existing cables are to be placed in split duct, encased in concrete, the cable shall be carefully located and exposed by hand tools.  Prior to being placed in duct, the Engineer shall be notified so that he may inspect the cable and determine that it is in good condition.  Where required, split duct shall be installed as shown on the drawings or as required by the Engineer.

110-3.3  CONDUITS WITHOUT CONCRETE ENCASEMENT.  Trenches for single-conduit lines shall be not less than 6 inches nor more than 12 inches wide, and the trench for 2 or more conduits installed at the same level shall be proportionately wider.  Trench bottoms for conduits without concrete encasement shall be made to conform accurately to grade so as to provide uniform support for the conduit along its entire length.

Unless otherwise shown on the plans, a layer of fine earth material, at least 4 inches thick (loose measurement) shall be placed in the bottom of the trench as bedding for the conduit.  The bedding material shall consist of soft dirt, sand or other fine fill, and it shall contain no particles that would be retained on a 1/4-inch sieve.  The bedding material shall be tamped until firm.  Flowable backfill may alternatively used.

Unless otherwise shown on plans, conduits shall be installed so that the tops of all conduits are at least 18 inches below the finished grade.

When two or more individual conduits intended to carry conductors of equivalent voltage insulation rating are installed in the same trench without  concrete encasement, they shall be spaced not less than 2 inches apart  (measured from outside wall to outside wall) in a horizontal direction and not less than 6 inches apart in a vertical direction.  Where two or more individual conduits intended to carry conductors of differing voltage insulation rating are installed in the same trench without concrete encasement, they shall spaced not less than 3 inches apart (measured from outside wall to outside wall) in a horizontal direction and lot less than 6 inches apart in a vertical direction.

Trenches shall be opened the complete length between normal termination points before conduit is installed so that if any unforeseen obstructions are encountered, proper provisions can be made to avoid them.

Conduits shall be installed using conduit spacers.  No. 4 reinforcing bars shall be driven vertically into the soil a minimum of 6 inches to anchor the assembly into the earth while backfilling.  For this purpose, the spacers shall be fastened down with locking collars attached to the vertical bars.  Spacers shall be installed at 5 -foot intervals.  Spacers shall be in the proper sizes and configurations to fit the conduits.  Locking collars and spacers shall be submitted to the Engineer for review prior to use.

110-3.4  MARKERS.  The location of each end and of each change of direction of conduits and duct banks shall be “marked” by a concrete slab marker 2 feet square and 4-6 inches thick extending approximately 1 inch above the surface.  The markers shall also be located directly above the ends of all conduits or duct banks, except where they terminate in a junction/access structure or building.

The Contractor shall impress the word “DUCT” or “CONDUIT” on each marker slab.  The Contractor shall also impress on the slab the number and size of conduits beneath the marker along with all other necessary information as determined by the Engineer.  The letters shall be 4 inches high and 3 inches wide with width of stroke 1/2-inch and 1/4-inch deep or as large as the available space permits.

Furnishing and installation of duct markers is incidental to the respective duct pay item.

110-3.5  BACKFILLING FOR CONDUITS.  For conduits, 8 inches of sand, soft earth, or other fine fill (loose measurement) shall be placed around the conduits ducts and carefully tamped around and over them with hand tampers.  The remaining trench shall then be backfilled and compacted in accordance with Item MO-152 "Excavation and Embankment" except that material used for back fill shall be select material not larger than 4 inches in diameter.

Flowable backfill may alternatively be used.

Trenches shall not contain pools of water during back, filling operations.

The trench shall be completely backfilled and tamped level with the adjacent surface: except that, where sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement.

Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

110-3.6  BACKFILLING FOR DUCT BANKS.  After the concrete has cured, the remaining trench shall be backfilled and compacted in accordance with Item MO-152 “Excavation and Embankment” except that the material used for backfill shall be select material not larger than 4 inches in diameter.  In addition to the requirements of MO-152, where duct banks are installed under pavement, one moisture/density test per lift shall be made for each 250 linear feet of duct bank or one work period's construction, whichever is less.

Flowable backfill may alternatively be used.

Trenches shall not contain pools of water during backfilling operations.

The trench shall be completely backfilled and tamped level with the adjacent surface:  except that, where sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement.

Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

110-3.7  RESTORATION.  Where soil and sod has been removed, it shall be replaced as soon as possible after the backfilling is completed.  All areas disturbed by work shall be restored to its original condition.  The restoration shall include any necessary topsoiling, fertilizing, liming, seeding, or mulching, as shown on the plans. All such work shall be performed in accordance with Item MO-901 “Seeding” and MO-908 “Mulching” or as directed by the Engineer.  The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.  Restoration shall be considered incidental to the pay item of which it is a component part.

METHOD OF MEASUREMENT

110-4.1  Underground conduits and duct banks shall be measured by the linear feet of conduits and duct banks installed, including encasement, locator tape, trenching and backfill with designated, resolution, and for drain lines, the termination at the drainage structure, all measured in place, completed, and accepted.  Separate measurement shall be made for the various types and sizes.

BASIS OF PAYMENT

110-5.1  Payment will be made at the contract unit price per linear foot for each type and size of conduit and duct bank completed and accepted, including trench and backfill with the designated material, and, for drain lines, the termination at the drainage structure.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item in accordance with the provisions and intent of the plans and specifications.

Payment will be made under:

Item MO-110-5.1.1	Airport [# and Size] PVC Concrete Encased Electrical Duct -- per linear foot

Item MO-110-5.1.2	Airport PVC Electrical Conduit [# and Size]-- per linear foot

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Engineer to specify the number and appropriate size of conduit.  If more than one size is required on the project, provide additional item nos.; one for each size and type.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

MATERIAL REQUIREMENTS

| Fed.Spec.W-C-1094 | Conduit and Conduit Fittings; Plastic, Rigid (cancelled; replaced by UL 514 Boxes, Nonmetallic Outlet, Flush Device Boxes, & Covers, and UL 651 Standard for Conduit & Hope Conduit, Type EB & A Rigid PVC) |
| --- | --- |
| Underwriters Laboratories Standard 6 | Rigid Metal Conduit |
| Underwriters Laboratories Standard 514B | Fittings for Cable and Conduit |
| Underwriters Laboratories Standard 1242 | Intermediate Metal Conduit |
| Underwriters Laboratories Standard 651 | Schedule 40 and 80 Rigid PVC Conduit (for Direct Burial) |
| Underwriters Laboratories Standard 651A | Type EB and A Rigid PVC Conduit and HDPE Conduit (for concrete encasement) |