### ITEM MO-108  UNDERGROUND POWER CABLE FOR AIRPORTS

DESCRIPTION

108-1.1  This item shall consist of furnishing and installing power cables direct buried and furnishing and/or installing power cables within conduit or duct banks in accordance with these specifications at the locations shown on the plans.  It includes excavation and backfill of trench for direct-buried cables only.  Also included are the installation of ground wires, ground rods and connections, cable splicing, cable marking, cable testing, and all incidentals necessary to place the cable in operating condition as a completed unit to the satisfaction of the Engineer.  This item shall not include the installation of duct banks or conduit, trenching and backfilling for duct banks or conduit, or furnishing or installation of any cable for FAA facilities.  Requirements and payment for trenching and backfilling for the installation of underground conduit and duct banks is covered under Item MO-110 “Airport Underground Electrical Duct Banks and Conduits.”

EQUIPMENT AND MATERIALS

108-2.1  GENERAL.

a.  Airport lighting equipment and materials covered by Federal Aviation Administration (FAA) specifications shall be approved under the Airport Lighting Equipment Certification Program described in Advisory Circular (AC) 150/5345-53, current version.

b.  All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification, when requested by the Engineer.

c.  Manufacturer's certifications shall not relieve the Contractor of the Contractor’s responsibility to provide materials in accordance with these specifications and acceptable to the Engineer.  Materials supplied and/or installed that do not materially comply with these specifications shall be removed, when directed by the Engineer and replaced with materials, which do comply with these specifications, at the sole cost of the Contractor.

d.  All materials and equipment used to construct this item shall be submitted to the Engineer for approval prior to ordering the equipment.  Submittals consisting of marked catalog sheets or shop drawings shall be provided.  Submittal data shall be presented in a clear, precise and thorough manner.  Original catalog sheets are preferred.  Photocopies are acceptable provided they are as good a quality as the original.  Clearly and boldly mark each copy to identify pertinent products or models applicable to this project.  Indicate all optional equipment and delete non-pertinent data.  Submittals for components of electrical equipment and systems shall identify the equipment for which they apply on each submittal sheet.  Markings shall be boldly and clearly made with arrows or circles (highlighting is not acceptable).  Contractor is solely responsible for delays in project accruing directly or indirectly from late submissions or resubmissions of submittals.

e.  The data submitted shall be sufficient, in the opinion of the Engineer, to determine compliance with the plans and specifications.  The Contractor's submittals (five (5) copies) shall be neatly bound in a properly sized 3-ring binder, tabbed by specification section.  The Engineer reserves the right to reject any and all equipment, materials or procedures, which, in the Engineer’s opinion, does not meet the system design and the standards and codes, specified herein.

f.  All equipment and materials furnished and installed under this section shall be guaranteed against defects in materials and workmanship for a period of at least twelve (12) months from final acceptance by the Owner.  The defective materials and/or equipment shall be repaired or replaced, at the Owner's discretion, with no additional cost to the Owner.  The Contractor shall be responsible to maintain an insulation resistance of 50 megohms minima, (1000V megger) with isolation transformers connected in new circuits and new segments of existing circuits through the end of the contract warranty period.

108-2.2  CABLE.  Underground cable for airfield lighting facilities (runway and taxiway lights and signs) shall conform to the requirements of AC 150/5345-7, Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits. Conductor sizes noted above shall not apply to leads furnished by manufacturers on airfield lighting transformers and fixtures.

Wire for electrical circuits up to 600 volts shall comply with Specification L-824 and/or Federal Specification J-C-30 and shall be type THWN-2.

Cable type, size, number of conductors, strand and service voltage shall be as specified on the plans.

108-2.3  BARE COPPER WIRE (GROUND) AND GROUND RODS.  Wire for ground installations for airfield lighting systems shall be No. 6 AWG solid or stranded conforming to ASTM B 3 and ASTM B 8, and shall be [bare copper] [tinned copper] wire conforming to the requirements of ASTM D 33.

Ground rods shall be [solid stainless steel] [copper] [copper-clad steel].  The ground rods shall be of the length and diameter specified on the plans but in no case shall they be less than 8-feet long nor less than 5/8 inch in diameter.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Engineer should evaluate the soils in the vicinity of proposed ground wire and ground rod installations and determine if soil conditions would adversely affect copper.  Engineer shall specify the type of ground rod and ground wire to be installed in consideration of the soil conditions.  If tinned copper ground wire is specified, include requirement for UL listing.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

108-2.4  EXOTHERMIC BONDING.  Bonding of ground wire to ground rods shall be by the exothermic welding process.  Only personnel experienced in and regularly engaged in this type of work shall make these connections.

Contractor shall demonstrate to the satisfaction of the Engineer, the welding kits, materials and procedures to be used for welded connections prior to any installations in the field.  The installations shall comply with the manufacturer's recommendations and the following:

All slag shall be removed from welds.

All buried copper and weld material at weld connections shall be thoroughly coated with 6 mil of 3M “Scotchkote,” or approved equivalent, or coated with coal tar bitumastic material to prevent surface exposure to corrosive soil or moisture.

108-2.5  CABLE CONNECTIONS.  In-line connections of underground primary cables shall be of the type called for on the plans, and shall be one of the types listed below.  No separate payment will be made for cable connections.

a.  The Cast Splice.  A cast splice, employing a plastic mold and using epoxy resin equivalent to that manufactured by Minnesota Mining and Manufacturing Company, “Scotchcast” Kit No. 82--B, or as manufactured by Hysol Corporation, “Hyseal Epoxy Splice” Kit No. E1135, or equivalent, is used for potting the splice is acceptable.

b.  The Field-attached Plug-in Splice.  Figure 3 of AC 150/5345-26, Specification for L-823 Plug and Receptacle, Cable Connectors, employing connector kits, is acceptable for field attachment to single conductor cable.  It shall be the Contractor’s responsibility to determine the outside diameter of the cable to be spliced and to furnish appropriately sized connector kits and/or adapters and heat shrink tubing with integral sealant.

c.  The Factory-Molded Plug-in Splice.  Specification for L-823 Connectors, Factory-Molded to Individual Conductors, is acceptable.

d.  The Taped or Heat-Shrinked Splice.  Taped splices employing field-applied rubber, or synthetic rubber tape covered with plastic tape is acceptable.  The rubber tape should meet the requirements of ASTM D 4388  and the plastic tape should comply with Mil Spec. MIL-I-24391or Fed. Spec. A-A-55809.  Heat shrinkable tubing shall be heavy-wall, self-sealing tubing rated for the voltage of the wire being spliced and suitable for direct-buried installations.  The tubing shall be factory coated with a thermoplastic adhesive-sealant that will adhere to the insulation of the wire being spliced forming a moisture- and dirt-proof seal.  Additionally, heat shrinkable tubing for multi-conductor cables, shielded cables, and armored cables shall be factory kits designed for the application.  Heat shrinkable tubing and tubing kits shall be manufactured by Tyco Electronics/ Raychem Corporation, Energy Division, or approved equivalent.

e.  In all the above cases, connections of cable conductors shall be made using crimp connectors utilizing a crimping tool designed to make a complete crimp before the tool can be removed.  All L-823 splices and terminations shall be made in accordance with the manufacturer’s recommendations and listings.

f.  All connections of grounding conductors and ground rods shall be made by the exothermic process or approved equivalent, except the base can ground clamp connector shall be used for attachment to the base can.  All exothermic connections shall be made in accordance with the manufacturer’s recommendations and listings.

108-2.6  SPLICER QUALIFICATIONS.  Every airfield lighting cable splicer shall be qualified in making cable splices and terminations on cables rated above 5,000 volts AC.  The Contractor shall submit to the Engineer proof of the qualifications of each proposed cable splicer for the cable type and voltage level to be worked on.  Cable splicing/terminating personnel shall have a minimum of three (3) years continuous experience in terminating/splicing medium voltage cable.

108-2.7  CONCRETE.  Concrete for cable markers shall conform to Specification Item MO-610, “Structural Portland Cement Concrete.”

108-2.8  FLOWABLE BACKFILL.  Flowable material used to backfill trenches for power cable trenches shall conform to the requirements of Item P-153 “Controlled Low Strength Material”.

108-2.9  TAPE.  Electrical tapes shall be Scotch Electrical Tapes – number Scotch 88 (1-1/2” wide) and Scotch 130C linerless rubber splicing tape (2” wide), as manufactured by the Minnesota Mining and Manufacturing Company, or approved equivalent.

108-2.10  ELECTRICAL COATING.  Scotchkote shall be as manufactured by Minnesota Mining and Manufacturing Company, or approved equivalent.

108-2.11  UNIT DUCT.  Unit duct shall be schedule 40 HDPE and shall comply with UL 651 B, NEMA TC-7, ASTM D 3485, ASTM F 2160 and ASTM D 3035.  The duct shall be annealed during the extrusion process. The duct shall be manufactured from black, virgin, high density polyethylene resin designated as Type III, Grade 3, Class C, Category 5 material in accordance with ASTM D 1248. The resin used in extruding the duct shall conform, as a minimum, to the ASTM Standards (latest edition) specified below, certified by the resin supplier on each lot of resin:

| Property | Value | ASTM Test |
| --- | --- | --- |
| Tensile Strength @ yield, psi | 3000 | D638 |
| Ultimate Elongation, % | 400 | D638 |
| Melt Index, gms/10min. | 0.5 max. | D1238 |
| Density of Base Resin, gms/cc | 0.941-0.955 | D1505 |
| Brittleness Temperature, F20, C Environmental Stress Crack | -75oC max. | D746 |
| Resistance, F20 | 96 hrs. | D1693 Cond. B, F10 |

Standard sizes of smooth wall polyethylene duct shall conform to the dimensional requirements specified below:

| Duct Size | Nominal Inside Diameter | Nominal Wall thickness | Nominal Outside Diameter |
| --- | --- | --- | --- |
| 1” | 1.049” | 0.133” | 1.315 |
| 1-1/4” | 1.380” | 0.140” | 1.660 |
| 1-1/2” | 1.610” | 0.145” | 1.900 |
| 2” | 2.067” | 0.154” | 2.375 |
| 2-1/2” | 2.469” | 0.203” | 2.875 |
| 3” | 3.040” | 0.216” | 3.500 |

Dimensional measurements shall be performed on samples removed from each length of finished duct. The manufacturer shall have the capability to manufacture a composite wire/cable-in-duct system wherein the wire and cables are placed in polyethylene duct without sticking during the extrusion process. The open ends of each length of reeled flexible duct shall be sealed by plastic caps to prevent the entrance of dirt and water. The duct shall have a durable identification, which shows the manufacturer’s name and/or trademark, all at intervals not to exceed ten (10) feet.

The manufacturer shall furnish copies of certified test reports on unit duct. The “unit duct” shall be as manufactured by Carlon Corporation or approved equivalent.

108-2.12  DETECTABLE WARNING TAPE.  Red plastic, detectable, magnetic tape shall be polyethylene film with a metallized foil core 4-6 inches wide and imprinted with the words “Caution Buried Electric Line Below”.  Detectable tape is incidental to the respective bid item.

108-2.13  EXISTING CIRCUITS.  Whenever the scope of work requires, connection to an existing circuit, the circuit’s insulation resistance shall be tested, in the presence of the Engineer.  The test shall be performed in accordance with this item and prior to any activity affecting the respective circuit.  The Contractor shall record the results on forms acceptable to the engineer.  When the work affecting the circuit is complete, the circuit’s insulation resistance shall be checked again, in the presence of the Engineer.  The Contractor shall record the results on forms acceptable to the engineer.  The second reading shall be equal to or greater than the first reading or the Contractor shall make the necessary repairs to the circuit to bring the second reading above the first reading.  All repair costs including a complete replacement of the L-823 connectors, L-830 transformers and L-824 cable, if necessary, shall be borne by the Contractor.  All test results shall be submitted in the Operation and Maintenance (O&M) Manual.

CONSTRUCTION METHODS

108-3.1  GENERAL.  The Contractor shall install the specified cable at the approximate locations indicated on the plans.  Unless otherwise shown on the plans, all cable required to cross under pavements expected to carry aircraft loads shall be installed in concrete encased duct banks.  Wherever possible, cable shall be run without splices, from connection to connection.

Cable connections between lights will be permitted only at the light locations for connecting the underground cable to the primary leads of the individual isolation transformers.  The Contractor shall be responsible for providing cable in continuous lengths for home runs or other long cable runs without connections, unless otherwise authorized in writing by the Engineer or shown on the plans.

In addition to connectors being installed at individual isolation transformers, L-823 cable connectors for maintenance and test points shall be installed at locations shown on the plans.  Cable circuit identification markers shall be installed on both sides of the L-823 connectors installed or at least once in each access point where L-823 connectors are not installed.

Provide not less than 3 feet of cable slack on each side of all connections, isolation transformers, light units, and at points where cable is connected to field equipment.  Where provisions must be made for testing or for future above grade connections, provide enough slack to allow the cable to be extended at least one foot vertically above the top of the access structure.  This requirement also applies where primary cable passes through empty base cans, junction and access structures to allow for future connections, or as designated by the Engineer.

108-3.2  INSTALLATION IN DUCT BANKS OR CONDUITS.  This item includes the installation of the cable in duct banks or conduit as described below.  The maximum number and voltage ratings of cables installed in each single duct or conduit, and the current-carrying capacity of each cable shall be in accordance with the latest National Electric Code, or the code of the local agency or authority having jurisdiction.

The Contractor shall make no connections or splices of any kind in cables installed in conduits or duct banks.

Unless otherwise designated in the plans, where ducts are in tiers, use the lowest ducts to receive the cable first, with spare ducts left in the upper levels.  Check duct routes prior to construction to obtain assurance that the shortest routes are selected and interferences are avoided.

Duct banks or conduits shall be installed as a separate item in accordance with Item MO-110, ``Airport Underground Electrical Duct Banks and Conduit.''  The Contractor shall run a mandrel through duct banks or conduit prior to installation of cable to insure that the duct bank or conduit is open, continuous and clear of debris.  Mandrel size shall be compatible with conduit size.  The Contractor shall swab out all conduits/ducts and clean base can, manhole, etc. interiors IMMEDIATELY prior to pulling cable.  Once cleaned and swabbed the base cans and all accessible points of entry to the duct/conduit system shall be kept closed except when installing cables.  Cleaning of ducts, base cans, manholes, etc. is incidental to the pay item of the item being cleaned.  All raceway systems left open, after initial cleaning, for any reason shall be recleaned at the Contractor’s expense.  All accessible points shall be kept closed when not installing cable.  The Contractor shall verify existing ducts proposed for use in this project as clear and open.  The Contractor shall notify the Engineer of any blockage in the existing ducts.  The cable shall be installed in a manner to prevent harmful stretching of the conductor, injury to the insulation, or damage to the outer protective covering.  The ends of all cables shall be sealed with moisture-seal tape providing moisture-tight mechanical protection with minimum bulk, or alternately, heat shrinkable tubing before pulling into the conduit and it shall be left sealed until connections are made.  Where more than one cable is to be installed in a conduit, all cable shall be pulled in the conduit at the same time.  The pulling of a cable through duct banks or conduits may be accomplished by handwinch or power winch with the use of cable grips or pulling eyes.  Maximum pulling tensions shall be governed by cable manufacturer’s recommendations.  A non-hardening lubricant recommended for the type of cable being installed shall be used where pulling lubricant is required.

The manufacturer's minimum bend radius or the NEC requirements whichever is more restrictive shall apply.  Cable installation, handling and storage shall be per manufacturer's recommendations.  During cold weather, particular attention shall be paid to the manufacturer's minimum installation temperature.  Cable shall not be installed when the temperature is at or below the manufacturer's minimum installation temperature.  At the Contractor’s option, the Contractor may submit a plan, for review by the Engineer, for heated storage of the cable and maintenance of an acceptable cable temperature during installation when temperatures are below the manufacturer’s minimum cable installation temperature.

Cable shall not be dragged across base can or manhole edges, pavement or earth.  When cable must be coiled, lay cable out on a canvas tarp or utilize other appropriate means to prevent abrasion to the cable jacket.

108-3.3  INSTALLATION OF DIRECT-BURIED CABLE IN TRENCHES.  The Contractor shall not use a cable plow for installing the cable.  Cable(s) shall be unreeled uniformly in place alongside or in the trench and shall be carefully placed along the bottom of the trench.  The cable(s) shall not be unreeled and pulled into the trench from one end.  Slack cable sufficient to provide strain relief shall be placed in the trench in a series of S curves.  Sharp bends or kinks in the cable shall not be permitted.

Where cables must cross over each other, a minimum of 3-inch vertical displacement shall be provided with the topmost cable depth at or below the minimum required depth below finished grade.

Primary airfield lighting cables installed shall have cable circuit identification markers attached on both sides of each L-823 connector and on each airport lighting cable entering or leaving cable access points, such as manholes, handholes, pullboxes, junction boxes, etc.  Markers shall be of sufficient length for imprinting the cable circuit identification legend on one line, using letters not less than ¼ inch in size.  The cable circuit identification shall match the circuits noted on the construction plans.

a. Trenching.  Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored.  Trenches for cables may be excavated manually or with mechanical trenching equipment.  Walls of trenches shall be essentially vertical so that a minimum of surface is disturbed.  Graders shall not be used to excavate the trench with their blades.  The bottom surface of trenches shall be essentially smooth and free from coarse aggregate.  Unless otherwise specified, cable trenches shall be excavated to a minimum depth of 18 inches below finished grade, except as follows:

(1)  When off the airport or crossing under a roadway or driveway, the minimum depth shall be 36 inches unless otherwise specified.

(2)  Minimum cable depth when crossing under a railroad track, shall be 42 inches unless otherwise specified.

Dewatering necessary for cable installation, erosion and turbidity control, in accordance with Federal, State, and Local requirements is incidental to its respective pay items as part of Item MO-108.  The cost of all excavation regardless of type of material encountered, shall be included in the unit price bid for the MO-108 Item.

The Contractor shall excavate all cable trenches to a width not less than 6 inches.  Unless otherwise specified on the plans, all cables in the same location and running in the same general direction shall be installed in the same trench.

When rock is encountered, the rock shall be removed to a depth of at least 3 inches below the required cable depth and it shall be replaced with bedding material of earth or sand containing no mineral aggregate particles that would be retained on a 1/4-inch sieve.  Flowable backfill material may alternatively be used.  The Contractor shall ascertain the type of soil or rock to be excavated before bidding.  All excavation shall be unclassified. Unclassified excavation will consist of the excavation of all material of whatever character encountered in the work.

Duct bank or conduit markers temporarily removed for trench excavations shall be replaced as required.

It is the Contractor’s responsibility to locate existing utilities within the work area prior to excavation.  Where existing active cable(s) cross proposed installations, the Contractor shall insure that these cable(s) are adequately protected.  Where crossings are unavoidable, no splices will be allowed in the existing cables, except as specified on the plans.  Installation of new cable where such crossings must occur shall proceed as follows:

(1)  Existing cables shall be located manually.  Unearthed cables shall be inspected to assure absolutely no damage has occurred.

(2)  Trenching, etc., in cable areas shall then proceed, with approval of the Engineer, with care taken to minimize possible damage or disruption of existing cable, including careful backfilling in area of cable.

In the event that any previously identified cable is damaged during the course of construction, the Contractor shall be responsible for the complete repair or replacement.

b. Backfilling.  After the cable has been installed, the trench shall be backfilled.  The first layer of backfill in the trench shall be 3 inches deep, loose measurement, and shall be either earth or sand containing no mineral aggregate particles that would be retained on a 1/4-inch sieve.  This layer shall not be compacted.  The second layer shall be 5 inches deep, loose measurement, and shall contain no particles that would be retained on a 1-inch sieve.  The remaining 3rd and subsequent layers of backfill shall not exceed 8 inches of loose measurement and be excavated or imported material and shall not contain stone or aggregate larger than 4 inches maximum diameter.

The second and subsequent layers shall be thoroughly tamped and compacted to at least the density of the adjacent undisturbed soil, and to the satisfaction of the Engineer.  If necessary to obtain the desired compaction, the backfill material shall be moistened or aerated as required.

Trenches shall not contain pools of water during backfilling operations.  The trench shall be completely backfilled and tamped level with the adjacent surface, except that when turf is to be established over the trench, the backfilling shall be stopped at an appropriate depth consistent with the type of turfing operation to be accommodated.  A proper allowance for settlement shall also be provided.  Any excess excavated material shall be removed and disposed of in accordance with the plans and specifications.

Underground electrical warning (caution) tape shall be installed in the trench above all direct-buried cable.  Contractor shall submit a sample of the proposed warning tape for acceptance by the Engineer.  If not shown on the plans, the warning tape shall be located six inches above the direct-buried cable.  A 4-6 inch wide polyethylene film detectable tape, with a metalized foil core, shall be installed above all direct buried cable.  The tape shall be of the color and have a continuous legend as indicated.  The tape shall be installed 8 inches minimum below finished grade.

c. Restoration.  Where soil and sod has been removed, it shall be replaced as soon as possible after the backfilling is completed.  All areas disturbed by work shall be restored to its original condition.  The restoration shall include any necessary topsoiling, fertilizing, liming, seeding, or mulching as shown on the plans. All such work shall be performed in accordance with Item MO-901 Seeding and MO-908 Mulching or as directed by the Engineer.  The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.  When trenching is through paved areas, restoration shall be equal to existing conditions and compaction shall meet the requirements of Item MO-152.  Restoration shall be considered incidental to the pay item of which it is a component part.

108-3.3  INSTALLATION OF CABLE IN UNIT DUCT.  In lieu of direct buried cable in trenches, at the contractor’s option, plowing-in of cable-in-unit duct shall be permitted at no additional cost to the contract. Plowing-in shall constitute the single pass operation of a) opening up the trench, b) installing the combination cable-in-unit duct in this trench, c) closing up the trench, and shall include d) equipment necessary to perform the operation.

The plowing equipment shall be of the vibratory type. It shall vibrate at a rate of at least 1200 cycles per minute. The vibrating unit shall not be rigidly mounted on a tractor. It shall be connected to the tractor for towing, in such a manner that the tractor will not dampen the vibrations.

The plow blade shall be of sufficient length to facilitate installation of the unit duct at the specified depth. The shoe throat shall be sized for the unit duct size. Cable way and cable guides shall be smooth, free of obstructions and sharp edges and shall not cause bending of the unit duct at shorter than 3-inch radius. It also shall not cause excessive cable strain, which may damage cable insulation or stretch the conductor.

The unit duct may be unreeled along the proposed cable route before plowing or the unit duct reels may be mounted on the tractor. In the latter case unreeling of the unit duct shall not cause excessive tension on the cable.

After the tractor and plow is positioned at the beginning of the run, sufficient unit duct slack shall be pulled through the throats. Then the plow shall be lowered into the hole and the unit duct shall be hand held for the start of plowing.

At each light hole the plow shall be stopped (movement and vibration), raised and the required amount of slack shall be hand pulled. Care shall be taken during this operation that the unit duct at the entrance into the light hole shall not be pulled from the specified depth. Plowing shall be continued by lowering the plow, starting it and holding by hand the unit duct until it is firmly held by the ground.

The plow shall not be backed onto the unit duct.

When an underground obstruction is encountered, the plow shall be lifted out of the ground. The obstruction shall be removed by hand digging. An opening shall be hand dug around the unit duct down to the depth of the unit duct and large enough to lower the plow. Then the plow shall be lowered into the opening. While this is being done the unit duct shall be pulled back into the throat by hand to prevent kinks and sharp bends. In no case shall the unit duct be bent sharper than 3 inch radius, or be subjected to excessive tension.

After installation of unit duct by plowing, the disturbed earth at the surface shall be leveled and, if necessary, compacted by a device approved by the Engineer.

Ends of cable shall be taped immediately after cutting to prevent moisture form entering the cable. Where the cable is not expected to be connected for at least 72 hours, the tape shall also be varnished.

Unit duct shall be terminated on the inside of light bases, handholes, and splice cans, or as close as possible to L-823 connectors at stake-mounted lights. Seal ends of unit duct to make watertight.

To identify routing of the unit duct, immediately after plowing, stakes shall be installed every 500 feet along straight runs and at each curve. Later these stakes shall be replaced by regular cable markers.

Before cable plowing is commenced, equipment to be used shall be inspected by the Engineer and approved. Before approving, the Engineer may require demonstration of the equipment at the installation site and location selected by the Engineer and by using actual unit duct. The test run shall consist of at least one starting hole, one intermediate hole (light location) and one terminating hole at least 100 feet long as a minimum. The test cable shall not be reused. The cost of the test run will be paid at the contract unit price.

Plow operators shall be experienced and qualified by schooling and/or by sufficient on-the-job training under an experienced operator. Proof of such qualification shall be required from the contractor.

108-3.4  CABLE MARKERS FOR DIRECT-BURIED CABLE.  The location of direct buried circuits shall be marked by a concrete slab marker, 2 feet square and 4-6 inches thick, extending approximately 1 inch above the surface.  Each cable run from a line of lights and signs to the equipment vault shall be marked at approximately every 200 feet along the cable run, with an additional marker at each change of direction of cable run.  All other direct-buried cable shall be marked in the same manner.  Cable markers shall be installed directly above the cable.  The Contractor shall impress the word “CABLE” and directional arrows on each cable marking slab.  The letters shall be approximately 4 inches high and 3 inches wide, with width of stroke 1/2 inch and 1/4 inch deep.

The location of each underground cable connection, except at lighting units, or isolation transformers, or power adapters shall be marked by a concrete marker slab placed above the connection.  The Contractor shall impress the word “SPLICE” on each slab.  The Contractor also shall impress additional circuit identification symbols on each slab as directed by the Engineer.  All cable markers and splice markers shall be painted international orange.  Paint shall be specifically manufactured for uncured exterior concrete.  Furnishing and installation of cable markers is incidental to the respective cable pay item.

108-3.5  SPLICING.  Connections of the type shown on the plans shall be made by experienced personnel regularly engaged in this type of work and shall be made as follows:

a.  Cast Splices.  These shall be made by using crimp connectors for jointing conductors.  Molds shall be assembled, and the compound shall be mixed and poured in accordance with manufacturer's instructions and to the satisfaction of the Engineer.

b.  Field-attached Plug-in Splices.  These shall be assembled in accordance with manufacturer's instructions.  These splices shall be made by plugging directly into mating connectors.  In all cases the joint where the connectors come together shall be wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches on each side of the joint.

c.  Factory-Molded Plug-in Splices.  These shall be made by plugging directly into mating connectors.  In all cases, the joint where the connectors come together shall be wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches on each side of the joint.

d.  Taped or Heat-Shrinked Splices.  A taped splice shall be made in the following manner:

Bring the cables to their final position and cut so that the conductors will butt.  Remove insulation and jacket allowing for bare conductor of proper length to fit compression sleeve connector with 1/4 inch of bare conductor on each side of the connector.  Prior to splicing, the two ends of the cable insulation shall be penciled using a tool designed specifically for this purpose and for cable size and type.  Do not use emery paper on splicing operation since it contains metallic particles.  The copper conductors shall be thoroughly cleaned.  Join the conductors by inserting them equidistant into the compression connection sleeve.  Crimp conductors firmly in place with crimping tool that requires a complete crimp before tool can be removed.  Test the crimped connection by pulling on the cable.  Scrape the insulation to assure that the entire surface over which the tape will be applied (plus 3 inches on each end) is clean.  After scraping wipe the entire area with a clean lint-free cloth.  Do not use solvents.

Apply high-voltage rubber tape one-half lapped over bare conductor.  This tape should be tensioned as recommended by the manufacturer.  Voids in the connector area may be eliminated by highly elongating the tape, stretching it just short of its breaking point.  Throughout the rest of the splice less tension should be used.  Always attempt to exactly half-lap to produce a uniform buildup.  Continue buildup to 1-1/2 times cable diameter over the body of the splice with ends tapered a distance of approximately 1 inch over the original jacket.  Cover rubber tape with two layers of vinyl pressure-sensitive tape one-half lapped.  Do not use glyptol or lacquer over vinyl tape as they react as solvents to the tape.  No further cable covering or splice boxes are required.

Heat shrinkable tubing shall be installed following manufacturer’s instructions.  Direct flame heating shall not be permitted unless recommended by the manufacturer.  Cable surfaces within the limits of the heat-shrink application shall be clean and free of contaminates prior to application.

108-3.8  TESTING.  The Contractor shall furnish all necessary equipment and appliances for testing the airport electrical systems and underground cable circuits before and after installation.  The Contractor shall perform all tests in the presence of the Engineer.  The Contractor shall demonstrate the electrical characteristics to the satisfaction of the Engineer.  All costs for testing are incidental to the respective item being tested.  For phased projects, the tests must be completed by phase and results meeting the specifications below must be maintained by the Contractor throughout the entire project as well as during the ensuing warranty period.

Earth resistance testing methods shall be submitted to the Engineer for approval.  Earth resistance testing results shall be recorded on an approved form and testing shall be performed in the presence of the Engineer.  All such testing shall be at the sole expense of the Contractor.

Should the ground grid conductors be damaged or suspected of being damaged by construction activities the Contractor shall test the conductors for continuity with a low resistance ohmmeter.  The conductors shall be isolated such that no parallel path exists and tested for continuity.  The Engineer shall approve of the test method selected.  All such testing shall be at the sole expense of the Contractor.

After installation, the Contractor shall test and demonstrate to the satisfaction of the Engineer the following:

a.  That all affected lighting power and control circuits (existing and new) are continuous and free from short circuits.

b.  That all affected circuits (existing and new) are free from unspecified grounds.

c.  That the insulation resistance to ground of all new non-grounded series circuits or cable segments is not less than 50 megohms.

d.  That the insulation resistance to ground of all non-grounded conductors of new multiple circuits or circuit segments is not less than 50 megohms.

e.  That all affected circuits (existing and new) are properly connected in accordance with applicable wiring diagrams.

f.  That all affected circuits (existing and new) are operable.  Tests shall be conducted that include operating each control not less than 10 times and the continuous operation of each lighting and power circuit for not less than 1/2 hour.

g. That the impedance to ground of each ground rod does not exceed 25 ohms prior to establishing connections to other ground electrodes.  The fall-of-potential ground impedance test shall be utilized, as described by ANSI/IEEE Standard 81, to verify this requirement.

Two copies of tabulated results of all cable tests performed shall be supplied by the Contractor to the Engineer.  Where connecting new cable to existing cable, ground resistance tests shall be performed on the new cable prior to connection to the existing circuit.

There are no approved "repair" procedures for items that have failed testing other than complete replacement.

METHOD OF MEASUREMENT

108-4.1  Trenching shall be measured by the linear feet of trench, including the excavation, backfill, and restoration, completed, measured as excavated, and accepted as satisfactory.

When specified, separate measurement shall be made for trenches of various specified widths.

The cost of all excavation, backfill, dewatering and restoration regardless of the type of material encountered shall be included in the unit price bid for the work.

108-4.2  Cable installed in trench, duct bank or conduit shall be measured by the number of linear feet of cable installed in trenches, duct bank or conduit, including ground rods and grounding connectors, and trench marking tape ready for operation, and accepted as satisfactory.  Separate measurement shall be made for each cable installed in trench, duct bank or conduit.  The measurement for this item shall not include additional quantities required for slack.

Cable slack is considered incidental to this item and is included in the contractor’s unit price.  No separate measurement or payment will be made for cable slack.

BASIS OF PAYMENT

108-5.1  Payment will be made at the contract unit price for trenching, cable installed in trench (direct-buried), or cable installed in duct bank or conduit, in place by the Contractor and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation and installation of these materials, and for all labor, equipment, tools, and incidentals, including ground rods and ground connectors and trench marking tape, necessary to complete this item.

Payment will be made under:

Item MO-108-5.1.1	Airport Type 1 Cable Trench -- per linear foot

Item MO-108-5.1.2	Airport Underground Cable (1/c, #[   ] AWG, 5KV), installed in trench, duct bank or conduit-- per linear foot

Item MO-108-5.1.2	Airport Underground Cable (1/c, #[   ] AWG, 600V), installed in trench, duct bank or conduit-- per linear foot

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Engineer to specify appropriate size of cable.  If more than one size is required on the project, provide additional item nos.; one for each size and type.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

MATERIAL REQUIREMENTS

AC 150/5345-7	Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-26	Specification for L-823 Plug and Receptacle Cable Connectors

FED SPEC J-C-30	Cable and Wire, Electrical Power, Fixed Installation (cancelled; replaced by A-A-59544 Cable and Wire, Electrical (Power, Fixed Installation))

FED SPEC A-A-55809	Insulation Tape, Electrical, Pressure-Sensitive Adhesive,

Plastic

ASTM B 3	Soft or Annealed Copper Wire

ASTM D 4388	Rubber tapes, Nonmetallic Semiconducting and Electrically Insulating

REFERENCE DOCUMENTS

NFPA No. 70	National Electrical Code (NEC)

MIL-S-23586C	Sealing Compound, Electrical, Silicone Rubber

Building Industry Consulting Service International (BICSI)

ANSI/IEEE Std 81	IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System